## FAN
Green Engineering Spreadsheets
Section-2 Dust and Pollution Collection
Copy write, © Green Engineering Spreadsheets 1 - Dust and Pollution, by John R Andrew,
2010-04-02
To scroll, roll the mouse wheel.
To zoom in, depress the Ctrl key and roll the mouse wheel away from you.
To open another, "Work Sheet Lesson" select a tab at the bottom of this spreadsheet.
To unlock the cells of this spreadsheet: Home > Format > Unprotect Sheet.
To lock the cells of this spreadsheet: Home > Format > Protect Sheet.
INDUSTRIAL FAN APPLICATIONS
CENTRIFUGAL FANS
Above image is at: http://www.engineeringtoolbox.com/fan-affinity-laws-d_196.html
Above data is at: http://www.engineeringtoolbox.com/fan-affinity-laws-d_196.html
CENTRIFUGAL FAN - AFFINITY LAWS
Air Volume Capacity (Q = cfm), Pressure Head, (P = in H2O), and Fan Power (HP = bhp)
relationship between similar fans.
| EXAMPLE: SPREADSHEET | [6 empty] | PROBLEM: SPREADSHEET
| Determine the: cu ft/min (cfm), in H2O, and bhp of fan B if the data below | [6 empty] | Determine the: cfm, in H2O, and bhp of fan B if the data below
| of fans A and B are given. | [6 empty] | of fans A and B are given.
|  |  |  | Input | [5 empty] | Input
|  |  | Fan (A) volume flow capacity, QA = | 2000 | cfm |  |  |  | Fan (A) volume flow capacity, QA = | 2000 | cfm
|  |  | Fan (A) pressure head, PA = | 0.5 | in H2O |  |  |  | Fan (A) pressure head, PA = | 0.5 | in H2O
|  |  | Fan (A) power, HPA = | 5 | bhp |  |  |  | Fan (A) power, HPA = | 5 | bhp
|  |  | Fan (A) wheel speed, NA = | 1750 | rpm |  |  |  | Fan (A) wheel speed, NA = | 1750 | rpm
|  |  | Fan (B) wheel speed, NB = | 1100 | rpm |  |  |  | Fan (B) wheel speed, NB = | 1100 | rpm
|  |  | Fan (A) wheel diameter, DA = | 2 | ft |  |  |  | Fan (A) wheel diameter, DA = | 2 | ft
|  |  | Fan (B) wheel diameter, DB = | 3 | ft |  |  |  | Fan (B) wheel diameter, DB = | 3 | ft
| Volume Capacity |  |  | Calculate |  |  |  | Volume Capacity |  | Calculate
|  |  | Fan (B) volume flow capacity, QB = | QA / [(NA / NB) * (DA / DB)^3] |  |  |  |  | Fan (B) volume flow capacity, QB = | QA / [(NA / NB) * (DA / DB)^3]
|  |  | = | 4242.8571 | cfm |  |  |  | = | 4242.8571 | cfm
| Head or Pressure | [6 empty] | Head or Pressure
|  |  | Fan (B) head or pressure, PB = | PA / [(NA / NB)^2 * (DA / DB)^2] |  |  |  |  | Fan (B) head or pressure, PB = | PA / [(NA / NB)^2 * (DA / DB)^2]
|  |  | = | 0.44449 | in H2O |  |  |  | = | 0.44449 | in H2O
| Power | [6 empty] | Power
|  |  | Fan (A) power, HPAw = | HPA * 746 |  |  |  |  | Fan (A) power, HPAw = | HPA * 746
|  |  | = | 3730 | Watts |  |  |  | = | 3730 | Watts
|  |  | Fan (B) power, HPB = | HPA / [(NA / NB)^3 * (DA / DB)^5] |  |  |  |  | Fan (B) power, HPB = | HPA / [(NA / NB)^3 * (DA / DB)^5]
|  |  | = | 14.1443 | bhp |  |  |  | = | 14.1443 | bhp
|  |  | HPBw = | 10551.648 | Watts |  |  |  | HPBw = | 10551.648 | Watts
EXAMPLE - "GOAL SEEK"
Determine the: cfm QA of fan A if the cfm QB of fan B is changed
| from 4243 cfm to 3000 cfm. |  |  | Input
|  |  | Fan (A) volume flow capacity, QA = | 1414.1414 | cfm
|  |  | Fan (A) pressure head, PA = | 0.5 | in H2O
|  |  | Fan (A) power, HPA = | 5 | bhp
|  |  | Fan (A) wheel velocity, NA = | 1750 | rpm
|  |  | Fan (B) wheel velocity, NB = | 1100 | rpm
|  |  | Fan (A) wheel diameter, DA = | 2 | ft
|  |  | Fan (B) wheel diameter, DB = | 3 | ft
| Volume Capacity |  |  | Calculate
|  |  | Fan (B) volume flow capacity, QB = | QA / [(NA / NB) * (DA / DB)^3]
|  |  | = | 3000 | cfm
Head or Pressure
|  |  | Fan (B) head or pressure, PB = | PA / [(NA / NB)^2 * (DA / DB)^2]
|  |  | = | 0.44449 | in H2O
Power
|  |  | Fan (A) power, HPAw = | HPA * 746
|  |  | = | 3730 | Watts
|  |  | Fan (B) power, HPB = | HPA / [(NA / NB)^3 * (DA / DB)^5]
|  |  | = | 14.1443 | bhp
|  |  | HPBw = | 10551.648 | Watts
Step-1: Select the cell contains a "Live" formula E161 containing the number 4243.
Step-2: Select dropdown menu: Data > What-If Analysis > Goal seek
Step-3: Type the desired value 3000 in the "To value: box as shown below.
Step-4: Pick the "By changing cell:" box with the mouse pointer.
Step-5: Pick the QA cell E152 containing the cfm number > OK.
Answer: QA changes from 2000 to 1414 cfm
QB has changed from 4243 to 3000 cfm
RECTANGULAR TO EQUIVALENT CIRCULAR AIR DUCT
Input
|  |  | Length of major side, A = | 36 | in
|  |  | Length of major minor side, B = | 24 | in
Calculate
|  |  | Equivalent diameter , De = | 1.30 * ((A * B)^0.625) / (A + B)^0.25)
|  |  | = | 31.9688 | in
ELLIPTICAL TO EQUIVALENT CIRCULAR AIR DUCT
Input
|  |  | Length of major axes, A = | 12 | in
|  |  | Length of major minor axes, B = | 6 | in
Calculate
|  |  | Cross-sectional area of oval duct , Ao = | π * A * B / 4
|  |  | = | 56.5488 | in^2
|  |  | Perimeter of an oval duct, P = | 2 * π * ((1/2) * (a^2 + b^2))^(1/2)
|  |  | = | 89.4115 | in
|  |  | Equivalent diameter, De ≈ | 1.55 * A^(0.625/P^0.2)
|  |  | ≈ | 4.3275 | in
CYCLONE AND BAGHOUSE
MAJOR FRICTION LOSS IN AIR DUCTS
Input
|  |  |  | Air volume flow, Q = | 15000 | cfm
|  |  |  | Equivalent (or actual) duct diameter, De = | 24 | inches diameter
|  |  |  | Total straight duct length (no branches), Ls = | 40 | ft (from sketch above)
|  |  |  | Total duct components equivalent length, Lc = | 16 | ft (from below)
Calculate
|  |  |  | Duct area, A = | π*De^2 / (4 * 144)
|  |  |  | = | 3.1416 | ft^2
|  |  |  | Air velocity, V = | Q / A
|  |  |  | = | 4774.6371 | ft/min
|  |  |  | Single duct length (no branches) + components, L = | Ls + Lc
[5 empty] | 56 | ft
|  |  |  | Major Friction (head or pressure loss), ΔP = | (0.109136 * Q^1.9) / De^5.02
|  |  |  | = | 1.0717 | inches water gauge/100 ft of duct
|  |  |  | Total friction (head or pressure loss), P = | ΔP * L / 100
|  |  |  | = | 0.60016 | inches water gauge
MINOR FRICTION LOSS IN AIR DUCTS
Input
|  |  | Flow velocity, V = | 3000 | ft/min
|  |  | Duct Component or Fitting: | 90 deg bend, rounded
radius/diameter duct >1
|  |  | Minor Loss Coefficient, f = | 0.25 | (from table below)
Calculate
|  |  | Flow velocity, v = | V / 60
|  |  | = | 50 | ft/sec
|  |  | Duct component equivalent length, Lc = | f * V^2 / (2 * g)
|  |  | = | 9.705 | ft of duct
Minor Loss Coef
|  |  | Duct Component or Fitting | f
|  |  | 90o bend, sharp | 1.3
|  |  | 90o bend, with vanes | 0.7
|  |  | 90o bend radius/diameter duct <1 | 0.5
|  |  | 90o bend, rounded | 0.25
|  |  | radius/diameter duct >1 | -
|  |  | 45o bend, sharp | 0.5
|  |  | Flow from duct to room | 1
|  |  | Flow from room to duct | 0.35
|  |  | Reduction, tapered | 0
|  |  | Grilles, 0.6 ratio free area to total surface | 4
|  |  | Grilles, 0.4 ratio free area to total surface | 10
|  |  | Grilles, 0.2 ratio free area to total surface | 50
SUM OF DUCT COMPONENT EQUIVALENT LENGTHS
|  | Duct Component | Equivalent Length Lc
|  | 1 | 9.7
|  | 2 | 4.5
|  | 3 | 2
4
6
7
8
9
10
|  | Total equiv. length, Lc = | 16.2 | ft
www.farrapc.com
Industrial Dust Collectors
Above image is at:
http://www.farrapc.com/
Above is the image at:
www.global-b2b-network.com/b2b/17/791/10821/b...
Above is the image at:
www.nauticexpo.com/prod/hi-air-korea/centrifu...
Above are images at: http://www.howden.com/en/Businesses/HowdenBuffalo
CHICAGO BLOWER
Above image is at:
http://www.chicagoblower.com/default.asp
AMAC
industrial centrifugal and in-line fan catalog:
http://www.canadianblower.com/
END OF "FAN APPLICATIONS" SECTION
DISCLAIMER: The materials contained in the online course are not intended as a representation or warranty on the part of PDHonline.org or any other person/organization named herein. The materials are for general information only. They are not a substitute for competent professional advice. Application of this information to a specific project should be reviewed by a registered professional engineer. Anyone making use of the information set forth herein does so at their own risk and assumes any and all resulting liability arising therefrom.
OVERVIEW OF THIS 4 PDH COURSE
Engineering Calculations with Spread Sheets
Engineering new or upgraded: dust collection equipment. The spreadsheets can facilitate optimum design.
Some advantages of spreadsheet calculations over hand written include:
1. easier to read.
2. better recall from archives.
3. greater accuracy.
4. faster with repeat use.
5. graphs are created automatically.
6. numerous useful formulas.
7. "Goal Seek" enables optimization.
8. solve any equation with, "Solver".
9. solve sets of linear and non-linear equations.
10. calculations and graphs may be pasted into
documents and slide show presentations.
Spread Sheet Method
Step-1 Open "Excel".
Step-2 Select drop-down menu, "View" > Toolbars > Drawing.
Step-3 Enter relevant data as shown below.
Step-4 Excel will perform the calculations.
Step-5 Copy the data and calculation cells and paste them into a project engineering spreadsheet.
Step-6 Optimize the calculation using Excel's, "Goal seek" as shown below.
Howden Buffalo Inc (North America)
Howden Buffalo supplies Howden fans, rotary heat exchangers, compressors and allied products to customers throughout the USA, Canada and Mexico.
Howden Buffalo’s experienced applications specialists, engineers, project managers, maintenance technicians and dedicated, highly skilled manufacturing professionals make it the industry leader in engineered fan systems in North America. The Buffalo in our name comes from the Buffalo Forge Fan Company, a highly respected name in North America established in 1877, and one of the many companies that have come to make up Howden Buffalo Inc. We have acquired the technology of over 25 fan companies, along with their extensive libraries of original drawings and specifications. So, in addition to new fans, we can provide replacement parts manufactured to meet the original fan designs. We can also offer upgrades and improvements to those original designs to increase efficiency, volume flow or pressure rise.
CENTRIFUGAL FANS A centrifugal fan is a mechanical device for moving air or gases. It has a fan wheel composed of a number of fan blades mounted around a hub. The gas enters from the side of the fan wheel, turns 90 degrees and accelerates due to centrifugal force as it flows over the fan blades and exits the fan housing.
Centrifugal fans can generate pressure rises in the gas stream. They are well-suited for industrial processes and air pollution control systems. They are also common in central heating/cooling systems
Fan components The major components of a typical centrifugal fan include the fan wheel, fan housing, drive mechanism, and inlet and/or outlet dampers. Direct Drive, above right.
The fan wheel can be linked directly to the shaft of an electric motor. This means that the fan wheel speed is identical to the motor's rotational speed. Belt Drive, right.
A set of sheaves are mounted on the motor shaft and the fan wheel shaft. The fan wheel speed is usually slower but may be faster than the motor's rotational speed.
Air Movement and Control Association (AMCA) The centrifugal fan performance tables provide the fan RPM and power requirements for the given CFM and static pressure at standard air density. When the centrifugal fan performance is not at standard conditions, the performance must be converted to standard conditions before entering the performance tables. Centrifugal fans rated by the (AMCA) are tested in laboratories with test setups that simulate installations that are typical for that type of fan. Usually they are tested and rated as one of four standard installation types as designated in AMCA Standard 210.
AMCA Standard 210 defines uniform methods for conducting laboratory tests on housed fans to determine airflow rate, pressure, power and efficiency, at a given speed of rotation. The purpose of AMCA Standard 210 is to define exact procedures and conditions of fan testing so that ratings provided by various manufacturers are on the same basis and may be compared. For this reason, fans must be rated in SCFM. Wikipedia Ratings found in centrifugal fan performance tables and curves are based on "Standard Cubic Feet per Minute" air SCFM. Fan manufacturers define standard air as clean, dry air with a density of 0.075 pounds mass per cubic foot (1.2 kg/m³), with the barometric pressure at sea level of 29.92 inches of mercury (101.325 kPa) and a temperature of 70°F (21°C). Selecting a centrifugal fan to operate at conditions other than standard air requires adjustment to both static pressure and power. The volume of air will not be affected in a given system because a fan will move the same amount of air regardless of the air density.
If, for example, a centrifugal fan moves 1,000 ft³/min (0.5 m³/s) at 70 °F (21 °C) it will also move 1,000 ft³/min (0.5 m³/s) at 200 °F (93 °C). Centrifugal fan air volume delivered by the centrifugal fan is not affected by density. However, since the 200 °F (93 °C) air weighs much less than the 70 °F (21 °C) air, the centrifugal fan will create less static pressure and will require less power. Wikipedia Selecting a centrifugal fan to operate at conditions other than standard air requires adjustment to both static pressure and power. When a centrifugal fan is specified for a given CFM and static pressure at conditions other than standard, an air density correction factor must be applied to select the proper size fan to meet the new condition. Since 200 °F (93 °C) air weighs only 80% of 70 °F (21 °C) air, the centrifugal fan will create less pressure. To get the actual pressure required at 200 °F (93 °C), the designer would have to multiply the pressure at standard conditions by an air density correction factor of 1.25 (i.e., 1.0/0.8) to get the system to operate correctly. To get the actual power at 200 °F (93 °C), the designer would have to divide the power at standard conditions by the air density correction factor. Wikipedia
CANADA BLOWER Manufacturers and distributors of industrial, process and commercial fans, blowers and ventilators. We supply different types of heating, ventilating and air-conditioning (HVAC) equipment. Industrial Fans and Blowers
Centrifugal Fans For General Ventilation
Capacities: to 500,000 CFM @ 100" WG Sizes: 5" to 85" Wheel Diameter Classes: I through V Arrangement: Belt Drive and Direct Drive Design Features: Choice of backward-inclined, airfoil, backward-curved or forward-curved wheel, all types of motors, drive guards, dampers and shutters, high temperature, spark-resistant / explosion proof construction. Service and Applications: General ventilating, light industrial, commercial air moving systems.
CHICAGO BLOWER
1675 Glen Ellyn Rd.
Glendale Heights, IL 60139
(630) 858-2600 Dirty Air Backward Inclined, Radial Tip and Radial Bladed fans. Rugged steel wheels are ideal for dust conveying or other industrial airstreams, erosive installations, and material handling applications.
INDUSTRIAL DUST COLLECTION APPLICATIONS Blasting - Chemical Processing - Fiber Glass - Laser Cutting - Mining - Paper Scrap - Pharmaceutical - Rubber Grinding - Seed Processing - Solar Panel Fabrication - Thermal/Flame Spray - Welding - Woodworking. For more information go to "Camfil Farr APC Corporation" at: http://www.farrapc.com/contact-us/.
FAN AFFINITY LAWS The spreadsheet cells below can be used to calculate fan: volume capacity, head, or power consumption - when speed or rpm, and wheel diameters are changed. Change in speed of wheel - revolutions per minute (rpm)
geometrically similarity - change in impeller diameter
Note that the affinity laws for pumps are not identical with fans.
Fan Affinity Laws
Volume Capacity
The volume capacity affinity law of similar centrifugal fans can be expressed:
Q1 / Q2 = (N1 / N2)(D1 / D2)3 (1)
where
Q = volume flow capacity (m3/s, cfm)
N = wheel velocity - revolution per minute - (rpm)
D = wheel diameter
Head or Pressure
The head or pressure of a centrifugal fan can be expressed like
P1 / P2 = (N1 / N2)2 (D1 / D2)2 (2)
where
P = Head or Pressure (inches water head)
Power
The power consumption of a centrifugal fan can be expressed as
P1 / P2 = (N1 / N2)3 (D1 / D2)5 (3)
where
P = Power (bhp)
Note: If the speed of a fan is increased with 10%
the volume flow increases with 10%
the head increases with 21%
the power increases with 33 %
Fan Affinity Laws Calculator - Changing Wheel Velocity
Replace the default values with the actual values. The calculator is generic and can be used with all common units as long as the use is consistent.
Changing the Impeller Diameter
If wheel velocity is constant a change in impeller diameter can simplify the affinity laws to
Volume Capacity
Q1 / Q2 = (D1 / D2)3
Head or Pressure
P1 / P2 = (D1 / D2)2
Power
P1 / P2 = (D1 / D2)5
Rectangular to Equivalent Circular Air Duct Determine circular equivalent of rectangular ducts. The equivalent diameter is the diameter of a circular duct or pipe that gives the same pressure loss as an equivalent rectangular duct or pipe. The equivalent diameter of a rectangular tube or duct can be calculated as (Huebscher)
De = 1.30 x ((A x B)0.625) / (A + B)0.25)
where
De = equivalent diameter (inches)
A = length of major side (inches)
B = length of minor side (inches)
Elliptical to Equivalent Circular Air Diameter
The equivalent diameter of a oval duct or tube (ellipse) can be calculated as (Heyt & Diaz)
De = 1.55 A0.625 / P0.2 (2)
where
A = cross-sectional area oval duct (m2, in2)
P = perimeter oval duct (m, inches)
The cross-sectional area of an oval duct can be expressed as
A = π A B / 4
where
a = major dimension of the flat oval duct (m, in)
b = minor dimension of the flat oval duct (m, in)
The perimeter of an oval duct can be expressed as
P ≈ 2 π (1/2 (a2 + b2))1/2 (2b)
Friction loss or major loss in ducts The major air friction loss, in a circular duct in galvanized steel with turbulent flow can for imperial units be expressed:
Δp = (0.109136 Q1.9) / De5.02 (1)
where
Δp = friction (head or pressure loss) (inches water gauge/100 ft of duct)
de = equivalent duct diameter (inches)
q = air volume flow - (cfm - cubic feet per minute)
For rectangular ducts the equivalent diameter must be calculated.
MINOR FRICTION LOSS IN AIR DUCTS Air flow and friction loss from a diagram is added to the major friction loss above. Minor pressure loss coefficients must be summarized for the actual applications.
Minor loss - pressure or head loss - coefficients for air duct distribution systems components Minor Loss - Head or Pressure Loss in Air Duct Components - can be expressed as:
Lcminor_loss = f V2/ 2 g
where:
Lcminor_loss = Minor Head Loss (ft)
f = Minor Loss Coefficient
v = Flow Velocity (ft/s)
g = Acceleration of Gravity (32.2 ft/s2)

## CYCLONE SEPARATION
Green Engineering Spreadsheets
Section-2 Dust and Pollution Collection
Copy write, © Green Engineering Spreadsheets 1 - Dust and Polution, by John R Andrew,
2010-04-02
To scroll, roll the mouse wheel.
To zoom in, depress the Ctrl key and roll the mouse wheel away from you.
To open another, "Work Sheet Lesson" select a tab at the bottom of this spreadsheet.
To unlock the cells of this spreadsheet: Home > Format > Unprotect Sheet.
To lock the cells of this spreadsheet: Home > Format > Protect Sheet.
CYCLONE PARTICLE SEPARATION
PARTICAL SIZE DISTRIBUTION
Input
|  |  | Metric Particle diameter, dm = | 10 | micro meters (meters/10^6)
Caculate
|  |  | US Particle diameter, di = | (dm/ 1000)/ 25.4
|  |  | = | 0.0003937 | inches (in)
|  |  | = | 393.7008 | micro inches
Cyclone Dust Collector Test Results
Inlet air velocity: Vi = 3200 ± 400 fpm
Particulate Loading Rate = 3 g/m^3 = 0.000187 lb/ft^3
Ambient temperature: 70°F and 35% relative humidity.
|  | Cyclone Dia (D) in |  | Pressure Drop |  | Collection Efficiency
|  | inch |  | in H2O |  | %
|  | 6 |  | 2.7 |  | 99.49
|  | 12 |  | 3.4 |  | 99.17
|  | 24 |  | 2.7 |  | 97.86
|  | 36 |  | 4 |  | 94.52
|  |  | Cyclone collection efficiency, E = | Mbin / (Mbin + Mfilter)
|  |  | Mbin = | mass of particle matter in cyclone bin
|  |  | Mfilter = | mass of particle matter in cyclone filter
|  |  | Cyclone collection efficiency, Ee = | Best fit experimental curve, R^2 = 1
|  |  | Ee = | -0.0001*D^3 + 0.0024*D^2 - 0.0638*D + 99.814
Input
|  |  | Cyclone diameter, D = | 12 | inches | D < 36 OK
Caculate
|  |  | Cyclone efficiency, Ee = | -0.0001*D^3 + 0.0024*D^2 - 0.0638*D + 99.814
|  |  | Ee = | 99.1 | %
EXPERIMENTAL CYCLONE COLLECTION EFFICIENCYS
Ref: (1) Perry's Chemical Engineers' Handbook, 6th Edition
Inlet Dust Particle Size Analysis
|  |  | Cumulative % Larger than Size Dp/Dc | Particle Diameter Dp (μm)
|  |  | 74 | 5
|  |  | 64 | 10
|  |  | 43 | 20
Input
|  |  |  | Cumulative % Larger than Dust Size, Dp/Dc = | 60 | %
Calculate
|  |  |  | Particle Diameter, Dp = | -0.4827*(Dp/Dc) + 40.789
|  |  |  | = | 11.827 | μm
|  |  |  | Particle Diameter, Dp = | 465.6299 | μ in
|  |  |  | Dp/Dc = | 0.6
|  |  |  | Fractional weight cyclone collection efficiency, η = | (Dp/Dc)^2 / (1 + (Dp/Dc)^2)
|  |  |  | = | 0.26471
|  |  |  | = | 26.4706 | %
Donaldson Torit
www.donaldsontorit.com
Donaldson Torit Fractional Efficiency Graph above.
Cyclone with Filter Bag Assembly
Above is the image at: pdf.directindustry.com/.../59006-80080.html
Flex-Kone™ CYCLONE DUST COLLECTORS
FARR Air Pollution Control
http://www.farrapc.com/
Above is the image at: www.materialhandlingequipments.in/pollution-c...
END OF, "CYLONE SEPARATION" SECTION
Left is the image at: www.flex-kleen.com/html/cycl_2.htm
In Flex-Kone™ cyclone dust collectors, centrifugal force separates suspended particles from the gas for high efficiency gas cleaning. The gas in introduced tangentially through the special involute inlet, producing a spiraling motion which directs solids entrained in the gas to the outer wall. The center core of clean gas is extracted through a concentric outlet tube. The dust continues down the wall of the outer tube into a sealed hopper from which it is collected without disrupting internal flow. Flex-Kleen 45 North Brandon Drive Glendale Heights, IL 60139 Toll Free: 1-800-621-0734 Phone: 630-775-0707 Fax: 630-295-9019 E-mail: info@flex-kleen.com
Steady State Cyclone Separator
As the cyclone is essentially a two phase particle-fluid system, fluid mechanics and particle transport equations can be used to describe the behaviour of a cyclone. The air in a cyclone is initially introduced tangentially into the cyclone with an inlet velocity Vin. Assuming that the particle is spherical, a simple analysis to calculate critical separation particle sizes can be established.
Given that the fluid velocity is moving in a spiral the gas velocity can be broken into two component velocities, a tangential component, Vt, and a radial velocity component Vr. Assuming Stokes' law, the drag force on any particle in this inlet stream is therefore given by the following equation:
Fd = 6πrpμVr.
Cyclonic separation is a method of removing particulates from an air, gas or water stream, without the use of filters, through vortex separation. Rotational effects and gravity are used to separate mixtures of solids and fluids.
A high speed rotating (air)flow is established within a cylindrical or conical container called a cyclone. Air flows in a spiral pattern, beginning at the top (wide end) of the cyclone and ending at the bottom (narrow) end before exiting the cyclone in a straight stream through the center of the cyclone and out the top. Larger (denser) particles in the rotating stream have too much inertia to follow the tight curve of the stream and strike the outside wall, falling then to the bottom of the cyclone where they can be removed. In a conical system, as the rotating flow moves towards the narrow end of the cyclone the rotational radius of the stream is reduced, separating smaller and smaller particles. The cyclone geometry, together with flow rate, defines the cut point of the cyclone. This is the size of particle that will be removed from the stream with a 50% efficiency. Particles larger than the cut point will be removed with a greater efficiency, and smaller particles with a lower efficiency.
An alternative cyclone design uses a secondary air flow within the cyclone to keep the collected particles from striking the walls to protect them from abrasion. The primary air containing the particulate enters from the bottom of the cyclone and is forced into spiral rotation by a stationary spinner. The secondary air flow enters from the top of the cyclone and moves downward toward the bottom, intercepting the particulate from the primary air. The secondary air flow also allows the collector to be mounted horizontally because it pushes the particulate toward the collection area.
Large scale cyclones are used in sawmills to remove sawdust from extracted air. Cyclones are also used in oil refineries to separate oils and gases, and in the cement industry as components of kiln preheaters. Smaller cyclones are used to separate airborne particles for analysis. Some are small enough to be worn clipped to clothing and are used to separate respirable particles for later analysis.
Analogous devices for separating particles or solids from liquids are called hydrocyclones. These may be used to separate solid waste from water in wastewater and sewage treatment. (Wikapedia)
If one considers an isolated particle circling in the upper cylindrical component of the cyclone at a rotational radius of r from the cyclone's central axis, the particle is therefore subjected to centrifugal, drag and buoyant forces. The centrifugal component is given by:
The buoyant force component is obtained by the difference between the particle and fluid densities, ρp and ρf respectively:
The force balance can be created by summing the forces together
This rate is controlled by the diameter of the particle's orbit around the central axis of the cyclone. A particle in the cyclonic flow will move towards either the wall of the cyclone, or the central axis of the cyclone until the drag, buoyant and centrifugal forces are balanced. Assuming that the system has reached steady state, the particles will assume a characteristic radius dependent upon the force balance. Heavier, denser particles will assume a solid flow at some larger radius than light particles. The steady state balance assumes that for all particles, the forces are equated, hence:
Fd + Fc + Fb = 0 Which expands to:
Gold Series® on Chemical Processing Applications
From ingestible powdered drugs to mouse poisons, the Gold Series works where other collectors fail.
Filter media selection is especially important for chemical processing, and each application will present specific concerns. Farr offers a variety of filter media choices. In addition, proper sizing and airflow calculations are crucial for a properly operating collection or recovery system.
Dust With Successful Dust Control Systems."
FARR Air Pollution Control 3505 South Airport Road Jonesboro, AR 72401 Phone: 870-933-8048 or Toll Free: 866-752-0702 Fax: 870-933-8381 Email: filterman@farrapc.com Saving energy and increasing production efficiency
while controlling indoor air quality is a challenging
aspect of plant management. Dust collectors– whether used for pollution control or product
recovery–can impact all these areas. Farr APC can help solve your dust problems.
WOOD WORKING above: There are several unique features of the
Gold Series® that makes it work so well
on wood and paper applications.
• The vertical arrangement and wide
spacing between the cartridges keep
material from bridging between them
and plugging the collector.
• Cartridge overbags keep large shavings
out of the cartridge pleat while allowing
the finer material to pass through to be
captured by the filter media.
• One cartridge will replace more than
10 bags when compared to a baghouse.
PAPER SCRAP SYSTEMS above:
Farr APC has literally hundreds of installations
for paper trim and scrap handling applications.
The Gold Series® is customized to accommodate
the fibrous nature of the dust. Typically a cyclone or screen separator drops scrap into a baler, and the GS filters the exhaust air from the cyclone or separator.
State-of-the-art manufacturing
• State-of-the art testing facilities
• Every piece of Farr APC equipment is
manufactured at an ISO 9001 certified facility.
• The most technologically advanced dust collection
systems on the market.
• Quality product from design to shipment.
• Three locations:
Collectors can be built in Jonesboro, Arkansas, USA;
Manchester, England; or Malaysia.
• Streamlined manufacturing through CNC production
equipment and certified welders.
• Guaranteed high quality dust collectors available…fast! • Engineers extensively
involved with indoor air
quality requirements.
• Fully-integrated manufacturing
process–we make the dust
collector and the filter
cartridges in-house.
Multiple-cyclone separators
Also known as multiclones, consist of a number of small-diameter cyclones, operating in parallel and having a common gas inlet and outlet, as shown in the figure. Multi-clones operate on the same principle as cyclones--creating a main downward vortex and an ascending inner vortex.
Multiclones are more efficient than single cyclones because they are longer and smaller in diameter. The longer length provides longer residence time while the smaller diameter creates greater centrifugal force. These two factors result in better separation of dust particulates. The pressure drop of multiclone collectors is higher than that of single-cyclone separators.
Mr. Prabhudas R. Aghera Darshini Engineers, Ahmedabad Plot No. 5227/A & B, Near Ramol Cross Road, Phase 4, G. I. D. C. Vatva Ahmedabad - 382 445, Gujarat, India Phone: +(91)-(79)-65436946 / 65456412 Fax: +(91)-(79)-25840556 Email: praghera@yahoo.co.in
Mechanical separator using centrifugal force to remove large and high-volume dust from industrial applications. An economical solution to a wide range of dust collection problems.
Excellent for high dust load, high temperature, and product recovery applications.
Can be used alone, with optional filter bag assembly, or as a pre-cleaner.
Applications from 300 to 13,000 cfm.
Heavy-duty construction for long life and low maintenance.
Meets seismic zone 4 and 100 mph wind load ratings.
Removable cone section for easy replacement.
Fractional Efficiency
Mechanical separator using centrifugal force to remove large and high-volume dust from industrial applications.
Fractional efficiency is the ratio of particles collected to particles entering the cyclone. This chart above shows the efficiency of a Cyclone collector with and without an optional filter bag assembly under clean, partial-load, and full-load conditions. Actual efficiency may vary dependingon the application. Dust concentration, airflow, particle shape, and density affect filtration efficiency.
Mineral Food/Pharmaceutical
● Cement ● Spray Dryer
● Lime ● Milling
● Gypsum ● Grinding
Chemical Energy
● Carbon Black ● Boilers
● TiO2 ● Incinerators
● Pigments
Cyclone Design Factors (Ref-1: Perry's Chemical Engineering Handbook , 6th edition) (Ref-2: Effects of Cyclone Diameter on Performance of 1D3D Cyclones: Collection Efficiency . Written for presentation at the 2006 ASABE Annual International Meeting Sponsored by: ASABE Oregon Convention Center, Portland, Oregon 9 - 12 July 2006) Cyclone diameter is the dominating efficiency control factor.
Texas A&M Cyclone Design (TCD) The Texas A&M Cyclone Design (TCD) method (Parnell, 1996) specifies cyclone dimensions based on the diameter (D) of the cyclone barrel as shown above. The barrel diameter is selected so that the volumetric flow rate of air (determined by the application) through the inlet cross-section (D/2 × D/4) results in the TCD design inlet velocity (975 ± 120 m/min [3200 ± 400 fpm] for 1D3D cyclones [Parnell, 1996]). The Ds in the 1D3D designation refer to the diameter of the cyclone barrel, while the numbers preceding the Ds refer to the relative length of the barrel and cone sections, respectively. Therefore, a 1D3D cyclone has a barrel length equal to the barrel diameter and a cone length equal to three times the barrel diameter.
Subsequently, given a value for Vt, possibly based upon the injection angle, and a cutoff radius, a characteristic particle filtering radius can be estimated, above which particles will be removed from the gas stream.
This can be expressed by rearranging the above in terms of the particle radius. The particle radius as a function of cyclonic radius, fluid density and fluid tangential and rotational velocities can then be found to be:
Experimentally it is found that the velocity component of rotational flow is proportional to r2[1], therefore:
This means that the established feed velocity controls the vortex rate inside the cyclone, and the velocity at an arbitrary radius is therefore:
A 1D3D cyclone with barrel length equal to the barrel diameter and a cone length equal to three times the barrel diameter as described above provided the following results:
Cyclone inlet velocity: 2640 ft/min (804 m/s) Cyclone pressure drop: 4 in H2O Inlet dust concentration: 2 - 5 gr/ft^3 (4.6 - 11.5 g/m^3) Note: 1 grain (gr). = 64.8 milligram; = 0.065 gram; = 0.35 ounce Specific gravity of dust: 3.0 (62.4 lb/ft^3) (1 g/cm^3) Gas: atmospheric air

## BAG HOUSE
Green Engineering Spreadsheets
Section-2 Dust and Pollution Collection
Copy write, © Green Engineering Spreadsheets 1 - Dust and Polution, by John R Andrew,
2010-04-02
To scroll, roll the mouse wheel.
To zoom in, depress the Ctrl key and roll the mouse wheel away from you.
To open another, "Work Sheet Lesson" select a tab at the bottom of this spreadsheet.
To unlock the cells of this spreadsheet: Home > Format > Unprotect Sheet.
To lock the cells of this spreadsheet: Home > Format > Protect Sheet.
BAGHOUSE COLLECTOR
Above is the image at: www.netl.doe.gov/.../healy/healyccdemo.html
The Babcock & Wilcox Company
Above is the image at: www.babcock.com/.../pulse_jet.html
Our environmental products include solutions for:
Mercury control
Nitrogen oxides control
Particulate and dust control
Replacement parts
Sulfur dioxide control
Sulfur trioxide control
Torit Cyclone Dust Collectors
http://www.industrialairsolutions.com/dust-collectors/torit-cyclone-dust-collector.htm
CCS. Click here to see an animation.
END OF, "BAGHOUSE COLLECTOR" SECTION
Fabric Filters
Commonly known as baghouses, fabric collectors use filtration to separate dust particulates from dusty gases. They are one of the most efficient and cost effective types of dust collectors available and can achieve a collection efficiency of more than 99% for very fine particulates.
Dust-laden gases enter the baghouse and pass through fabric bags that act as filters. The bags can be of woven or felted cotton, synthetic, or glass-fiber material in either a tube or envelope shape.
The high efficiency of these collectors is due to the dust cake formed on the surfaces of the bags. The fabric primarily provides a surface on which dust particulates collect through the following four mechanisms:
Inertial collection - Dust particles strike the fibers placed perpendicular to the gas-flow direction instead of changing direction with the gas stream.
Interception - Particles that do not cross the fluid streamlines come in contact with fibers because of the fiber size. Brownian Movement
- Submicrometre particles are diffused, increasing the probability of contact between the particles and collecting surfaces.
Electrostatic forces - The presence of an electrostatic charge on the particles and the filter can increase dust capture.
A combination of these mechanisms results in formation of the dust cake on the filter, which eventually increases the resistance to gas flow. The filter must be cleaned periodically.
Midwesco® Filter Resources, Inc. is a global industrial air filtration leader based in Winchester, VA. The company manufactures and distributes air filter elements in 100 market segments across six continents. We maintain a large diversified inventory of high quality custom made dust collector and baghouse filter bags, cartridge filters, pleated elements, and baghouse accessories in our global manufacturing facilities residing in Winchester, VA; Bolingbrook, IL; Nakskov, Denmark, and Nigel, South Africa for critical delivery. Midwesco Filter Resources, Inc. P.O. Box 2075 (22604) 385 Battaile Drive Winchester, VA 22601 Toll Free 800.336.7300 http://www.midwescofilter.com/CaseStudies.aspx?ID=12
Thermo+Plus® Pleated Elements - Coal-Fired Industrial Boiler
This plant’s boiler was load-limited and could not sustain full load operations. Midwesco/TDC through it's Thermo+Plus® Pleated Elements were able to increase capacity to maximum output.
Coal Fired Industrial BoilerSouthwest, US
Highlights:• 39% increase in flow; from 287,000 to 401,000 ACFM.• 14.7% drop in average module delta-P. • 4.2% reduction in opacity per ACFM
• On-time installation, exceeded estimated performance and within budget.
Problem: This plant’s boiler was load-limited and could not sustain full load operations. They were baghouse-limited, running at +8” delta P and could not maximize the boiler operations due to the limited baghouse flows. Solution: Midwesco introduced Thermo+Plus® pleated elements, using PPS media with ePTFE membrane. We also provided upgraded Mecair® high-capacity pulse valves that increased the cleaning capacity by more than 47%. Midwesco provided turn-key service, including product, installation, and start-up assistance. Results: The boiler can now operate at its maximum output with lower cost-per-cfm at the baghouse. The plant now operates at full load boiler capacity.
Expanding Baghouse Capabilities Using Fabric Technology
Problem:
This plant was experiencing a bottleneck at the pulse-jet baghouse, and could not operate the coal fired boiler at full load. This limited the plant capacity during the annual sugar campaign. The baghouse was operating at 14” – 15” DP. The plant was actively considering the purchase of a new, larger baghouse. Solution:
Midwesco introduced our 651TEX woven fiberglass with ePTFE membrane to solve this problem. 651TEX uses a micro-porous ePTFE Membrane to enhance air flows, reduce media drag and enhance ash release. Results:
Midwesco supplied new cages, a full compartment of 651TEX filter bags, and technical assistance on operating parameters for the baghouse system. This plant can now operate the boiler at maximum capacity with existing equipment, avoiding a large capital expenditure for a larger baghouse. Follow-up Data:
1. Plant operating at full boiler capacity.
2. Baghouse operates at 4” – 7” DP.
3. Cleaning system operations reduced 45%, equals longer bag life.
4. Opacity excursions eliminated.
5. Lower usage of compressed air, and lower costs.
US Department of Energy Project illustrated above. Participant Alaska Industrial Development and Export Authority
Location Healy, Denali Borough, AK (adjacent to Healy Unit No. 1)
Plant Capacity/Production 50 MWe (nominal)
Technology TRW's Clean Coal Combustion System; Babcock & Wilcox's spray dryer absorber (SDA) with sorbent recycle
Coal Usibelli subbituminous 50% run-of-mine (ROM) coal and 50% waste coal CCPI/Clean Coal Demonstrations Healy Clean Coal Project
Advanced Electric Power Generation Advanced Combustion/Heat Engines Project Funding
Total cost: $242,058,000 100% DOE: $117,327,000 48% Participant: $124,731,000 52%
Project Objective To demonstrate an innovative new power plant design featuring integration of an advanced combustor coupled with both high- and low-temperature emissions control processes. Technology/Project Description Emissions are controlled using TRW's clean coal combustion system, an advanced entrained/slagging combustor through staged fuel and air injection for NOx control and limestone injection for SO2 control. Additional SO2 is removed using B&W's activated recycle SDA. A coal-fired precombustor increases the air inlet temperature for optimum slagging performance. The slagging combustors are bottom mounted, injecting the combustion products into the boiler. The main slagging combustor consists of a water-cooled cylinder that slopes toward a slag opening. The precombustor burns 25%-40% of the total coal input. The remaining coal is injected axially into the combustor, rapidly entrained by the swirling precombustor gases and additional air flow, and burned under substoichiometric conditions for NOx control. The ash forms molten slag, which flows along the water-cooled walls and is driven by aerodynamic and gravitational forces through a slot into the slag recovery section. About 70%-80% of the ash is removed as molten slag. The hot gas is then ducted to the furnace where, to ensure complete combustion, additional air is supplied from a tertiary air windbox to NOx ports and to final overfire air ports. Pulverized limestone (CaCO3 ) for SO2 control is fed into the combustor where it is flash calcined (converting CaCO3 to lime [CaO]). The mixture of this CaO and ash that was not removed in the combustor, called flash-calcined material, is removed in the fabric filter system. Most of the flash-calcined material is used to form a 45% solids slurry, which is injected into the spray dryer. The SO2 in the flue gas reacts with the slurry droplets as water is simultaneously evaporated. The SO2 is further removed from the flue gas by reacting with the dry flash-calcined-material on the baghouse filter bags. Results Summary
Environmental
NOx emissions ranged from 0.208–0.278 lb/106 Btu, with typical emissions of 0.245 lb/106 Btu on a 30-day rolling average, which is well below the permit limit of 0.350 lb/106 Btu on a rolling day average.
SO2 emissions were consistently less than 0.09 lb/106 Btu, with typical emissions of 0.038 lb/106 Btu, which are below the permit limit of 0.10 lb/106 Btu (3-hour average).
High SO2 removal efficiencies in excess of 90% were achieved with low-sulfur coal and Ca/S molar ratios of 1.4–1.8.
Particulate matter (PM) emissions were 0.0047 lb/106 Btu, which is well below the permit limit of 0.020 lb/106 Btu.
CO emissions were less than 130 ppm at 3.0% O2, with typical emissions of 20–50 ppm at 3.0% O2, which is well below the permit limit of 202 ppm at 3.0% O2.
Tests showed that the SDA system SO2 emissions, PM emissions, and opacity were well within guarantees of the technology supplier. Operational
Carbon burnout goals for the technology supplier were achieved—greater than 99% carbon burnout at 100% maximum continuous rating (MCR) for the ROM, 50/50 blend of ROM/ waste coal, and 55/45 blend. The carbon burnout was typically 99.7%.
The contract goal of the technology supplier for slag recovery greater than 70% at 100% MCR for all coals was also achieved. Slag recovery ranged from 78–87%, with a typical recovery of 83%.
During a 90-day test in the second half of 1999, the plant availability was 97% at a capacity factor of 95%.
The SDA pressure drops and power consumption were well below guarantee levels of the technology supplier.
The system required less limestone and produced less solid waste by-product than anticipated. Economic
The capital costs of a 50-MWe and 300-MWe plant using this system are $90.6 million ($1,812/kW) and $450.7 million ($1,502/kW) (1993$), respectively.
The variable operating costs for the 300-MWe system are $7.2 million/yr (1993$) for the fixed cost and $28.4 million/yr (1993$) for the variable costs (based on 90% capacity factor).
The levelized cost of power is 36.5 mills/kWh (constant 1993$) for the 300-MWe plant (based on 90% capacity factor).
The levelized cost per ton of SO2/NOx removed is $6,499/ton (constant 1993$) for the 300 MWe plant (based on 90% capacity factor).
Design features: Multiple compartment enclosure with each compartment containing up to several thousand long, vertically supported, small diameter fabric bags; the gas passes through the porous bag material which separates the particulate from the flue gas; bags are cleaned by a pulse of compressed air.
Applicable boiler sizes: 25 MW to 1300 MW.
Removal efficiencies: To 99.9+%.
Fuels: Coal and municipal solid waste.
MAILING ADDRESS:
The Babcock & Wilcox Company 800 Main Street, 4th Floor Lynchburg, VA 24504 U.S.A. Above is the image at: www.babcock.com/.../pulse_jet.html
PHONE:
434.522.6000 (Lynchburg, Va.) B&W Nuclear Operations Group, Inc. B&W Technical Services Group, Inc.
434.522.6800 (Lynchburg, Va.) Corporate B&W Nuclear Power Generation Group, Inc.
330.753.4511 (Barberton, Ohio) B&W Power Generation Group, Inc. (Fossil/Environmental/Renewable) Reliable steam generation must be accomplished with the lowest allowable impact on the environment.
B&W integrates environmental protection systems into its new boiler and power plant installations as well as existing plants to help our customers meet tough environmental regulations.
Our continued research and commercial development of new technologies have led to many advancements in air pollution control. We provide a variety of proven emissions control technologies, both combustion and post-combustion.
Dust Collectors, Industrial Vacuum Cleaners, Mist Collection Systems, HEPA Air Cleaners, 1-877-844-3293 NEW scrubber technology incorporates charged water droplets to collect 99.99% of particulates to 0.1µ using just 600 watts.
In a Cloud Chamber Scrubber, billions of droplets and particles move continuously in relation to each other.
As they approach 10 microns of separation, electrical attraction causes the particulate to enter the droplets.
This means that collector water droplets are delivered to the particulate in a way that has never been accomplished before. This fact is critical in understanding the function of the CCS.
CCS offers several advantages over conventional devices used for submicron control. Chief among them is the requirement of less than 1" of pressure drop per CCS stage under full load operation.
By contrast, venturi systems typically require 40" to 70" of pressure drop; diffusion candles typically require 16" to 20" of pressure drop. This factor is a major contributor to the CCS system’s low operating costs. Wet or dry, ESP equipment power requirements are over 100 times greater.
Another distinguishing feature of the CCS is its ability to remove fumes and gases, including HCl, HF, HNO3, H2SO4, SO2, Cl2 and NH3, and others simultaneously with particulate. This is important because now one device can handle submicron particulate and hazardous fumes simultaneously. In practical terms, this gives management the ability to eliminate the maintenance costs and labor associated with packed towers.
The CCS has been shown to be 99.99%+ efficient for the collection of all types of particulate from 0.1 to 300+ microns. Systems are manufactured to customers’ specifications in UV-stabilized polypropylene, FRP, PVC, 304 and 316 stainless steel, and higher alloy materials such as Hastelloy.

## ELECTROSTATIC
Green Engineering Spreadsheets
Section-2 Dust and Pollution Collection
Copy write, © Green Engineering Spreadsheets 1 - Dust and Polution, by John R Andrew,
2010-04-02
To scroll, roll the mouse wheel.
To zoom in, depress the Ctrl key and roll the mouse wheel away from you.
To open another, "Work Sheet Lesson" select a tab at the bottom of this spreadsheet.
To unlock the cells of this spreadsheet: Home > Format > Unprotect Sheet.
To lock the cells of this spreadsheet: Home > Format > Protect Sheet.
ELECTROSTATIC PRECIPITATOR
Above is the image at: www.electrofilter.com/Paper/paper_06.htm
Top View of ESP Schematic Diagram [Source: Powerspan Corp.].
Electrostatic Precipitator Design Calculator
Air Pollution Control (1)
| Precipitator Type | Dust Type | Gas Flow Rate ft^3/min | Average Gas Velocity ft/sec | Electrodes Collecting Area ft^2 | Overall Collector Efficiency% | Particle Drift Velocity ft/sec
| Rod Curtain | Smelter Fume | 180000 | 6 | 44400 | 85 | 0.13
| Tulip Type | Gypsum from Kiln | 25000 | 3.5 | 3800 | 99.7 | 0.64
| Perforated Plate | Flt Ash | 108000 | 6 | 10900 | 91 | 0.4
| Rod Curtain | Cement | 204000 | 9.5 | 26000 | 91 | 0.31
Ref: (1) Perry's Chemical Engineers' Handbook, 6th Edition
(2) P. Aarne Vesilind, J. Jeffrey Peirce and Ruth F. Weiner. 1994.
Environmental Engineering, Butterworth Heinemann. 3rd ed.
|  |  |  | Input |  | Calculate
|  |  | Gas flow rate, Q = | 25000 | ft^3/min = | 11.75 | meter^3/min
|  |  | Particle drift velocity, Vd = | 0.64 | ft/sec = | 0.19507 | meter/sec
|  |  | Electrodes collecting area, A = | 3800 | ft^2 = | 353.02 | meter^2
Electrostatic Precipitator
Collection Efficiency Estimate, R = 1 - e^(-A*Vd / Q) is for one particle size.
Overall efficiency is obtained by integrating actual dust particle size distribution.
| (1) Given: Q, Vd, and A, find R |  |  | Input
|  |  | Gas flow rate (fpm), Q = | 90000 | ft^3/min
|  |  | Particle drift velocity, Vd = | 0.4 | ft/sec
|  |  | Electrodes collecting area, A = | 10000 | ft^2
Calculation
|  |  | Gas flow rate (fps), q = | 1500 | ft^3/sec
|  |  | e = | 2.7183
|  |  | Collection efficiency estimate, R = | 1 - e^(-A*Vd / q)
|  |  | = | 0.93052
|  |  | = | 93.05%
| (2) Given: R, Vd, and A, find Q |  |  | Input
|  |  | Collection efficiency estimate, R = | 95 | %
|  |  | Particle drift velocity, Vd = | 0.4 | ft/sec
|  |  | Electrodes collecting area, A = | 19971.5485 | ft^2
Calculation
|  |  | e = | 2.7183
|  |  | R = | 0.95
|  |  | (1 - R) = | 0.05
|  |  | Gas flow rate (fps), q = | -A*Vd / ln(1 - R)
|  |  | q = | 2666.6667 | ft^3/sec
|  |  | Q = | 160000 | ft^3/min
Above equations are at: http://www.ajdesigner.com/phpprecipitator/electrostatic_precipitator_equation_collection_efficiency.php
Collection Efficiency Estimate, R = 1 - e^(-A*Vd / Q) is for one partical size.
Overall efficiency Ro% is obtained by integrating actual dust particle
size distribution. Area A is equal to area B above.
For a more detailed overview of an electrostatic precipitator, see Powerspan Corp.
(formerly Zero Emmisions Technology) homepage at
www.powerspancorp.com/news/precipitator.shtml
which also includes a couple of nice schematics.
Photographs of electrostatic precipitators at coal-fired power plants can be found at
http://www4.ncsu.edu/~frey/apcespph.html.
WET ELECTROSTATIC PRECIPITATOR
Above is the image at: www.directindustry.com/prod/allied-blower-she...
END OF, "ELECTROSTATIC PRECIPITATOR" SECTION
An electrostatic precipitator (ESP), or electrostatic air cleaner is a particulate collection device that removes particles from a flowing gas (such as air) using the force of an induced electrostatic charge. Electrostatic precipitators are highly efficient filtration devices that minimally impede the flow of gases through the device, and can easily remove fine particulate matter such as dust and smoke from the air stream.[1]. In contrast to wet scrubbers which apply energy directly to the flowing fluid medium, an ESP applies energy only to the particulate matter being collected and therefore is very efficient in its consumption of energy (in the form of electricity). Wikapedia
Collection efficiency (R)
Precipitator performance is very sensitive due to two particulate properties: 1) Resistivity; and 2) Particle size distribution. These properties can be determined economically and accurately in the laboratory. A widely taught concept to calculate the collection efficiency is the Deutsch model, which assumes infinite remixing of the particles perpendicular to the gas stream.
Resistivity can be determined as a function of temperature in accordance with IEEE Standard 548. This test is conducted in an air environment containing a specified moisture concentration. The test is run as a function of ascending or descending temperature or both. Data are acquired using an average ash layer electric field of 4 kV/cm. Since relatively low applied voltage is used and no sulfuric acid vapor is present in the environment, the values obtained indicate the maximum ash resistivity.
Usually the descending temperature test is suggested when no unusual circumstances are involved. Before the test, the ash is thermally equilibrated in dry air at 850°F for about 14 hours. It is believed that this procedure anneals the ash and restores the surface to pre-collection condition.
If there is a concern about the effect of combustibles, the residual effect of a conditioning agent other than sulfuric acid vapor, or the effect of some other agent that inhibits the reaction of the ash with water vapor, the combination of the ascending and descending test mode is recommended. The thermal treatment that occurs between the two test modes is capable of eliminating the foregoing effects. This results in ascending and descending temperature resistivity curves that show a hysteresis related to the presence and removal of some effect such as a significant level of combustibles.
With particles of high resistivity (cement dust for example) Sulfur trioxide is sometimes injected into a flue gas stream to lower the resistivity of the particles in order to improve the collection efficiency of the electrostatic precipitator .
Modern industrial electrostatic precipitators ESPs continue to be excellent devices for control of many industrial particulate emissions, including smoke from electricity-generating utilities (coal and oil fired), salt cake collection from black liquor boilers in pulp mills, and catalyst collection from fluidized bed catalytic cracker units in oil refineries to name a few. These devices treat gas volumes from several hundred thousand ACFM to 2.5 million ACFM (1,180 m³/s) in the largest coal-fired boiler applications. For a coal-fired boiler the collection is usually performed downstream of the air preheater at about 320 deg.F which provides optimal resistivity of the coal-ash particles. For some difficult applications with low-sulfur fuel hot-end units have been built operating above 700 deg.F.
The original parallel plate–weighted wire design (described above) has evolved as more efficient (and robust) discharge electrode designs were developed, today focusing on rigid (pipe-frame) discharge electrodes to which many sharpened spikes are attached (barbed wire), maximizing corona production. Transformer-rectifier systems apply voltages of 50–100 kilovolts at relatively high current densities. Modern controls, such as an automatic voltage control, minimize sparking and prevent arcing (sparks are quenched within 1/2 cycle of the TR set), avoiding damage to the components. Automatic plate-rapping systems and hopper-evacuation systems remove the collected particulate matter while on line, theoretically allowing ESPs to stay in operation for years at a time.
Electrostatic Precipitators for Power Plants
Many countries around the world, including our own, depend on coal and other fossil fuels to produce electricity. A natural result from the burning of fossil fuels, particularly coal, is the emission of flyash. Ash is mineral matter present in the fuel. For a pulverized coal unit, 60-80% of ash leaves with the flue gas. Historically, flyash emissions have received the greatest attention since they are easily seen leaving smokestacks.
Two emission control devices for flyash are the traditional fabric filters and the more recent electrostatic precipitators. The fabric filters are large baghouse filters having a high maintenance cost (the cloth bags have a life of 18 to 36 months, butcan be temporarily cleaned by shaking or backflushing with air). These fabric filters are inherently large structures resulting in a large pressure drop, which reduces the plant efficiency. Electrostatic precipitators have collection efficiency of 99%, but do not work well for flyash with a high electrical resistivity (as commonly results from combustion of low-sulfur coal). In addition, the designer must avoid allowing unburned gas to enter the electrostatic precipitator since the gas could be ignited.
The salt & pepper collector/selector, and repelling balloon experiments serve to illustrate the basis of an electrostatic precipitator. In these experiments a type of electrostatic collector and electrostatic selector are created. This same principle is used to keep the environment clean today.
The fluegas laden with flyash is sent through pipes having negatively charged plates which give the particles a negative charge. The particles are then routed past positively charged plates, or grounded plates, which attract the now negatively-charged ash particles. The particles stick to the positive plates until they are collected. The air that leaves the plates is then clean from harmful pollutants.
Wet Electrostatic Precipitator (WESP) Allied Blower Sheet Metal Ltd
For more go to: www.alliedblower.com Wet electrostatic precipitator (WESP) systems are recognized as the most reliable devices for removal of sub-micron sized solid particles and liquid droplets form the gas stream. The down-flow/up-flow WESP-2F is the most efficient and reliable WESP when dealing with heavy loading of solid and sticky particles and eliminating carry over of fine mist and droplets.
A wet electrostatic precipitator (WESP or wet ESP) operates with saturated air streams (100% relative humidity). One type of WESP uses a vertical cylindrical tube with centrally-located wire electrode (gas flowing upward) with water sprays to clean the collected particulate from the collection surface (plates, tubes). The collected water and particulate forms a wet film slurry that eliminates the resistivity issues associated with dry ESP's. Another type of WESP (used for coke-oven gas detarring) uses a falling oil film to remove collected material.
Electrostatic Precipitator KnowledgeBase Particle Size An electrostatic precipitator collects particles most easily when the particle size is coarse. The generation of the charging corona in the inlet field may be suppressed if the gas stream has too many small particles (less than 1 µm). Very small particles (0.2 - 0.4µm) are the most difficult to collect because the fundamental field-charging mechanism is overwhelmed by diffusion charging due to random collisions with free ions. For more go to: http://www.neundorfer.com/knowledge_base/electrostatic_precipitators.aspx

## UNITS
Green Engineering Spreadsheets
Section-2 Dust and Pollution Collection
Copy write, © Green Engineering Spreadsheets 1 - Dust and Polution, by John R Andrew,
2010-04-02
To scroll, roll the mouse wheel.
To zoom in, depress the Ctrl key and roll the mouse wheel away from you.
To open another, "Work Sheet Lesson" select a tab at the bottom of this spreadsheet.
UNIT CONVERSION
http://www.matweb.com/tools/unitconverter.aspx
| To Convert From: | To: | Multiply By:
| lbf/in2 (psi) | pascal (Pa) | 6894.757
| pascal (Pa) | lbf/in2 (psi) | 0.00014504
| g/cm3 | lb/ft3 | 62.428
| lb/ft3 | kg/m3 | 16.0185
| lb/in3 | kg/m3 | 27679.9
| lb/ft3 | g/cm3 | 0.016018
| volts/mil | kV/mm | 0.03937
| mil (0.001 inch) | cm | 0.00254
| cm | mil | 393.7
| MPa(m1/2) | psi(in1/2) | 910.06
| J/(g-°C) | BTU/(lb-°F) | 0.23901
| BTU/(lb-°F) | J/(g-°C) | 4.184
| joule (J) | cal (thermochemical) | 0.23901
| cal (thermochemical) | joule (J) | 4.184
| joule (J) | BTU (thermochemical) | 0.00094845
| BTU (thermochemical) | joule | 1054.35
| µm/(m-°C) | µin/(in-°F) | 0.55556
| µin/(in-°F) | µm/(m-°C) | 1.8
| cm3/Kg | in3/lb | 0.02768
| in3/lb | cm3/kg | 36.127
| W/(m K) | BTU in /(hr ft2 F) | 6.9335
| BTU in /(hr ft2 F) | W/(m K) | 0.14413
| (J m)/(min m2 C) | W/(m-K) | 0.016667
| W/(m-K) | (J m)/(min m2 C) | 60
© MatWeb: This table may be copied, but the copyright and hyperlink to MatWeb must not be removed.
US to Metric Units
|  | Convert: | 0.000187 | lb/ft3
|  | To: | kg/m3
|  | Multiply By: | 16.0185
|  | Answer: | 0.0029955 | kg/m3
Metric to US Units
|  | Convert: | 0.003 | kg/m3
|  | To: | lb/ft3
|  | Divide By: | 16.0185
|  | Answer: | 0.00018728 | lb/ft3
1 meter = 39.3700787 inches
1 micrometer = 39.3700787 micro-inches
Input
|  | Particle Diameter, Dp = | 1 | (μm)
Calculate
|  | Particle Diameter, Dp = | 39.3701 | (μ in)
Note: 1 grain (gr). = 64.8 milligram; = 0.065 gram; = 0.35 ounce
END OF, "UNIT CONVERTION" SECTION
MatWeb has also provided a reference table for converting between English and Metric units.